## Compression cost
Energy cost for air compression
| Compressor Data | Value | Input Data in Green Cells
| Motor KW | 5
| Compressor capacity M3 / min | 2
| Operational hours per year | 6000
| Energy Cost € /kwatt-hr | 0.0652
| Full load motor efficiency | 90%
| Total cost energy per year | 2173.3333
| Total cubic meter per year | 720000
| Energy cost per 1000 cubic meter | 3.0185
SDT can not be held responsible for the use of this calculator
Resulta are approximate

## Air lost per orifices
[5 empty] | Pressure | SCFM | bar | m3/min
PSI
[5 empty] | 2 | 0.1548 | 0.13789 | 0.0043834 | 0.0049537
Air lost based on diameter orifice and line pressure |  |  |  |  | 5 | 0.2554 | 0.34474 | 0.0072321 | 0.00683
[8 empty] | 0 | 0.0037
Input Data |  |  |  |  | 10 | 0.3862 | 0.68947 | 0.010936 | 0.0099457
[5 empty] | 15 | 0.502 | 1.0342 | 0.014215 | 0.013047
Orifice diameter | Pressure | Hrs / year | Air lost | Cost € / year | 20 | 0.6094 | 1.3789 | 0.017256 | 0.016134
Ф (mm) | (bar) |  | (M3/min) |  | 25 | 0.7149 | 1.7237 | 0.020244 | 0.019207
[5 empty] | 30 | 0.8195 | 2.0684 | 0.023206 | 0.022266
1 | 8 | 6000 | 0.07096 | 77.1099 | 35 | 0.9221 | 2.4132 | 0.026111 | 0.02531
[5 empty] | 40 | 1.0232 | 2.7579 | 0.028974 | 0.02834
[5 empty] | 45 | 1.1242 | 3.1026 | 0.031834 | 0.031356
| Conversion from inches to mm |  |  |  | 50 | 1.2264 | 3.4474 | 0.034728 | 0.034358
[5 empty] | 70 | 1.6242 | 4.8263 | 0.045992 | 0.046222
| Inches |  | mm |  | 80 | 1.8242 | 5.5158 | 0.051656 | 0.052068
[5 empty] | 90 | 2.0237 | 6.2053 | 0.057305 | 0.057858
Diameter Ф | 0.041667 |  | 1.0583 |  | 100 | 2.2226 | 6.8947 | 0.062937 | 0.06359
[5 empty] | 125 | 2.7172 | 8.6184 | 0.076942 | 0.077671
[5 empty] | 150 | 3.2099 | 10.3421 | 0.090894 | 0.091396
SDT can not be held responsible for the use of this calculator |  |  |  |  | 200 | 4.1972 | 13.7895 | 0.11885 | 0.11778

## With SDT170+flex@0,4m
SDT can not be held responsible for the use of this calculator
Leaks Cost Calculator using SDT 170 system |  |  |  |  | Type of sensor : |  | Internal or flexible
Pressure in line : |  | 1 to 6 bar |  |  | Distance from leak : |  |  | 0,4 m |  | Total leak rate |  | 7.5509 | M³/hour
Input Cells |  | hr / year : | 6000 | [6 empty] | Cost a year |  | 136.7554
Leak # | dBµV | Litre/hour |  | Leak # | dBµV | Litre/hour |  | Leak # | dBµV | Litre/hour | Leak # | dBµV |  | Litre/hour
1 | 77 | 3190 |  | 13 |  | 0 |  | 25 |  | 0 | 37 |  |  | 0
2 | 9 | 0 |  | 14 |  | 0 |  | 26 |  | 0 | 38 |  |  | 0
3 | 10 | 81.8136 |  | 15 |  | 0 |  | 27 |  | 0 | 39 |  |  | 0
4 | 60 | 1259.1517 |  | 16 |  | 0 |  | 28 |  | 0 | 40 |  |  | 0
5 | 76 | 3019.9439 |  | 17 |  | 0 |  | 29 |  | 0 | 41 |  |  | 0
6 |  | 0 |  | 18 |  | 0 |  | 30 |  | 0 | 42 |  |  | 0
7 |  | 0 |  | 19 |  | 0 |  | 31 |  | 0 | 43 |  |  | 0
8 |  | 0 |  | 20 |  | 0 |  | 32 |  | 0 | 44 |  |  | 0
9 |  | 0 |  | 21 |  | 0 |  | 33 |  | 0 | 45 |  |  | 0
10 |  | 0 |  | 22 |  | 0 |  | 34 |  | 0 | 46 |  |  | 0
11 |  | 0 |  | 23 |  | 0 |  | 35 |  | 0 | 47 |  |  | 0
12 |  | 0 |  | 24 |  | 0 |  | 36 |  | 0 | 48 |  |  | 0
Range limit : 10 to 76 dB

## With SDT170+flex@2m
SDT can not be held responsible for the use of this calculator
Leaks Cost Calculator using SDT 170 system |  |  |  |  | Type of sensor : |  | Internal or flexible
Pressure in line : |  | 1 to 10 bar |  |  | Distance from leak : |  |  | 2 m |  | Total leak rate |  | 19.8229 | M³/hour
Input Cells |  | hr / year : | 6000 | [6 empty] | Cost a year |  | 359.014
Leak # | dBµV | Litre/hour |  | Leak # | dBµV | Litre/hour |  | Leak # | dBµV | Litre/hour | Leak # | dBµV |  | Litre/hour
1 | 10 | 224.6838 |  | 13 |  | 0 |  | 25 |  | 0 | 37 |  |  | 0
2 | 9 | 0 |  | 14 |  | 0 |  | 26 |  | 0 | 38 |  |  | 0
3 | 71 | 5930 |  | 15 |  | 0 |  | 27 |  | 0 | 39 |  |  | 0
4 | 70 | 5621.1631 |  | 16 |  | 0 |  | 28 |  | 0 | 40 |  |  | 0
5 | 11 | 237.0696 |  | 17 |  | 0 |  | 29 |  | 0 | 41 |  |  | 0
6 | 60 | 3286.8794 |  | 18 |  | 0 |  | 30 |  | 0 | 42 |  |  | 0
7 | 65 | 4298.3817 |  | 19 |  | 0 |  | 31 |  | 0 | 43 |  |  | 0
8 | 10 | 224.6838 |  | 20 |  | 0 |  | 32 |  | 0 | 44 |  |  | 0
9 |  | 0 |  | 21 |  | 0 |  | 33 |  | 0 | 45 |  |  | 0
10 |  | 0 |  | 22 |  | 0 |  | 34 |  | 0 | 46 |  |  | 0
11 |  | 0 |  | 23 |  | 0 |  | 35 |  | 0 | 47 |  |  | 0
12 |  | 0 |  | 24 |  | 0 |  | 36 |  | 0 | 48 |  |  | 0
Limit : 10 to 70 dB

## With SDT170+Para@2m
SDT can not be held responsible for the use of this calculator
Leaks Cost Calculator using SDT 170 system |  |  |  |  | Type of sensor : |  | Parabolic Dish | [7 empty] | dBµV | L/h
[15 empty] | 65 | 756
Pressure in line : |  | 1 to 10 bar |  |  | Distance from leak : |  |  | 2 m |  | Total leak rate |  | 14.031 | M³/hour |  | 65.5 | 805
[15 empty] | 66 | 855
Input Cells |  | hr / year : | 6000 | [6 empty] | Cost a year |  | 254.117 |  |  | 66.5 | 905
[15 empty] | 67 | 956
[15 empty] | 67.5 | 1007
Leak # | dBµV | Litre/hour |  | Leak # | dBµV | Litre/hour |  | Leak # | dBµV | Litre/hour | Leak # | dBµV |  | Litre/hour | 68 | 1059
[15 empty] | 68.5 | 1112
1 | 64 | 0 |  | 13 |  | 0 |  | 25 |  | 0 | 37 |  |  | 0 | 69 | 1165
[15 empty] | 69.5 | 1219
2 | 65 | 756 |  | 14 |  | 0 |  | 26 |  | 0 | 38 |  |  | 0 | 70 | 1274
[15 empty] | 70.5 | 1329
3 | 87 | 4125 |  | 15 |  | 0 |  | 27 |  | 0 | 39 |  |  | 0 | 71 | 1385
[15 empty] | 71.5 | 1442
4 | 88 | 4550 |  | 16 |  | 0 |  | 28 |  | 0 | 40 |  |  | 0 | 72 | 1500
[15 empty] | 72.5 | 1558
5 | 89 | 4600 |  | 17 |  | 0 |  | 29 |  | 0 | 41 |  |  | 0 | 73 | 1618
[15 empty] | 73.5 | 1678
6 |  | 0 |  | 18 |  | 0 |  | 30 |  | 0 | 42 |  |  | 0 | 74 | 1740
[15 empty] | 74.5 | 1802
7 |  | 0 |  | 19 |  | 0 |  | 31 |  | 0 | 43 |  |  | 0 | 75 | 1866
[15 empty] | 75.5 | 1930
8 |  | 0 |  | 20 |  | 0 |  | 32 |  | 0 | 44 |  |  | 0 | 76 | 1996
[15 empty] | 76.5 | 2063
9 |  | 0 |  | 21 |  | 0 |  | 33 |  | 0 | 45 |  |  | 0 | 77 | 2132
[15 empty] | 77.5 | 2202
10 |  | 0 |  | 22 |  | 0 |  | 34 |  | 0 | 46 |  |  | 0 | 78 | 2274
[15 empty] | 78.5 | 2347
11 |  | 0 |  | 23 |  | 0 |  | 35 |  | 0 | 47 |  |  | 0 | 79 | 2422
[15 empty] | 79.5 | 2499
12 |  | 0 |  | 24 |  | 0 |  | 36 |  | 0 | 48 |  |  | 0 | 80 | 2580
[15 empty] | 80.5 | 2660
Limit : 65 to 88 dB | [14 empty] | 81 | 2744
[15 empty] | 81.5 | 2831
[15 empty] | 82 | 2920
[15 empty] | 82.5 | 3013
[15 empty] | 83 | 3110
[15 empty] | 83.5 | 3211
[15 empty] | 84 | 3318
[15 empty] | 84.5 | 3429
[15 empty] | 85 | 3548
[15 empty] | 85.5 | 3674
[15 empty] | 86 | 3810
[15 empty] | 86.5 | 3959
[15 empty] | 87 | 4125
[15 empty] | 87.5 | 4317
[15 empty] | 88 | 4550

## With SDT170+Para@5m
SDT can not be held responsible for the use of this calculator
Leaks Cost Calculator using SDT 170 system |  |  |  |  | Type of sensor : |  | Parabolic Dish | [7 empty] | dBµV | L/h
[15 empty] | 56 | 944
Pressure in line : |  | 1 to 10 bar |  |  | Distance from leak : |  |  | 5 m |  | Total leak rate |  | 14.825 | M³/hour |  | 56.5 | 998
[15 empty] | 57 | 1053
Input Cells |  | hr / year : | 6000 | [6 empty] | Cost a year |  | 268.4972 |  |  | 57.5 | 1108
[15 empty] | 58 | 1164
[15 empty] | 58.5 | 1221
Leak # | dBµV | Litre/hour |  | Leak # | dBµV | Litre/hour |  | Leak # | dBµV | Litre/hour | Leak # | dBµV |  | Litre/hour | 59 | 1278
[15 empty] | 59.5 | 1336
1 | 54 | 0 |  | 13 |  | 0 |  | 25 |  | 0 | 37 |  |  | 0 | 60 | 1396
[15 empty] | 60.5 | 1455
2 | 77 | 4776 |  | 14 |  | 0 |  | 26 |  | 0 | 38 |  |  | 0 | 61 | 1516
[15 empty] | 61.5 | 1578
3 | 76 | 4305 |  | 15 |  | 0 |  | 27 |  | 0 | 39 |  |  | 0 | 62 | 1632
[15 empty] | 62.5 | 1704
4 | 56 | 944 |  | 16 |  | 0 |  | 28 |  | 0 | 40 |  |  | 0 | 63 | 1769
[15 empty] | 63.5 | 1835
5 | 78 | 4800 |  | 17 |  | 0 |  | 29 |  | 0 | 41 |  |  | 0 | 64 | 1902
[15 empty] | 64.5 | 1970
6 |  | 0 |  | 18 |  | 0 |  | 30 |  | 0 | 42 |  |  | 0 | 65 | 2039
[15 empty] | 65.5 | 2110
7 |  | 0 |  | 19 |  | 0 |  | 31 |  | 0 | 43 |  |  | 0 | 66 | 2183
[15 empty] | 66.5 | 2257
8 |  | 0 |  | 20 |  | 0 |  | 32 |  | 0 | 44 |  |  | 0 | 67 | 2332
[15 empty] | 67.5 | 2410
9 |  | 0 |  | 21 |  | 0 |  | 33 |  | 0 | 45 |  |  | 0 | 68 | 2489
[15 empty] | 68.5 | 2570
10 |  | 0 |  | 22 |  | 0 |  | 34 |  | 0 | 46 |  |  | 0 | 69 | 2654
[15 empty] | 69.5 | 2740
11 |  | 0 |  | 23 |  | 0 |  | 35 |  | 0 | 47 |  |  | 0 | 70 | 2829
[15 empty] | 70.5 | 2921
12 |  | 0 |  | 24 |  | 0 |  | 36 |  | 0 | 48 |  |  | 0 | 71 | 3016
[15 empty] | 71.5 | 3114
Limit : 56 to 77 dB | [14 empty] | 72 | 3217
[15 empty] | 72.5 | 3325
[15 empty] | 73 | 3437
[15 empty] | 73.5 | 3556
[15 empty] | 74 | 3682
[15 empty] | 74.5 | 3817
[15 empty] | 75 | 3964
[15 empty] | 75.5 | 4125
[15 empty] | 76 | 4305
[15 empty] | 76.5 | 4515
[15 empty] | 77 | 4776

## Total leaks cost
Total Cost of leaks based on compressor operation |  |  |  | Total Cost of leaks found with SDT170 system
Charging time (minutes) |  |  | 10 | Type of sensor : | Internal or flexible 0,4m |  | 136.7554
Time between charges (minutes) |  |  | 10 |  | Internal or flexible 2m |  | 359.014
Compressor capacity M³ / min |  |  | 2 |  | Parabolic Dish 2m |  | 254.117
Operational hours per year |  |  | 6000 |  | Parabolic Dish 5m |  | 268.4972
System leakage rate in M³/ min |  |  | 1
Total cost leakage a year |  |  | 1086.6667 |  |  | TOTAL COST | 1018.3836
Number of equivalent leaks with Ф | 1 | mm | 14.0924
SDT can not be held responsible for the use of this calculator

## Hoja1 (hidden)
leak Dmm | CFM
0.4 | 0.45
0.79 | 1.6
1.19 | 3.66
1.59 | 6.45
2.38 | 14.5
3.2 | 25.8
4.8 | 58.3
6.4 | 103
7.8 | 162
9.5 | 234